## Sheet1
Flow(m^3/h) | Head(m) |  | Quantity | Value or formula
0 | 15.6 |  | D (m) | 0.1
20 | 15.5 |  | L (m) | 95
40 | 15.3 |  | ε roughness (m) | 4.57e-05
60 | 14.3 |  | ρ (kg/m³) | 997
80 | 12.4 |  | μ (kg/m·s) | 0.000891
96 | 9.6 |  | Q_ref (m³/h) | 71
|  |  | A (m²) | 0.007854
|  |  | v (m/s) | 2.5111
|  |  | Re | 280985.1841
|  |  | f0 (starting guess) | 0.018167
|  |  | f1 | 0.018049
|  |  | f2 (Colebrook) | 0.018054
|  |  | k (m/(m³/h)²) | 0.0010935
|  |  | k_s | 5.7551e-05
77.8499

## Sheet2
Flow | Pump curve | pipe line | flow | 70.5958
0 | 15.6 | 8 | pump curve | 13.4499
8 | 15.5531 | 8.07 | pipe line | 13.4496
16 | 15.5254 | 8.2799 | difference | 0.00034236
24 | 15.4866 | 8.6298
32 | 15.4058 | 9.1197
40 | 15.2526 | 9.7495
48 | 14.9963 | 10.5193
56 | 14.6063 | 11.4291
64 | 14.0521 | 12.4788
72 | 13.303 | 13.6685
80 | 12.3285 | 14.9982
88 | 11.0979 | 16.4678
96 | 9.5807 | 18.0774

## Sheet3
Flow | system curve(9m static head) | pump curve | Flow guess | 66.5201
0 | 9 | 15.6 | pump head | 13.8386
8 | 9.07 | 15.5531 | pipe head | 13.8385
16 | 9.2799 | 15.5254 | difference | 9.1583e-05
24 | 9.6298 | 15.4866
32 | 10.1197 | 15.4058
40 | 10.7495 | 15.2526
48 | 11.5193 | 14.9963
56 | 12.4291 | 14.6063
64 | 13.4788 | 14.0521
72 | 14.6685 | 13.303
80 | 15.9982 | 12.3285
88 | 17.4678 | 11.0979
96 | 19.0774 | 9.5807

## Sheet4
Flow | dirty pipe, k = 0.002 | Pump curve | Flow guess | 57.2019
0 | 8 | 15.6 | pump head | 14.5441
8 | 8.128 | 15.5531 | pipe head | 14.5441
16 | 8.512 | 15.5254 | difference | -3.0729e-05
24 | 9.152 | 15.4866
32 | 10.048 | 15.4058
40 | 11.2 | 15.2526
48 | 12.608 | 14.9963
56 | 14.272 | 14.6063
64 | 16.192 | 14.0521
72 | 18.368 | 13.303
80 | 20.8 | 12.3285
88 | 23.488 | 11.0979
96 | 26.432 | 9.5807

## Sheet5
PV | 3.2 | Flow | Npsha | hf_suction | NPSHR | Margin | Ratio | TEMP | pv | rho | NPSHA | margin | ratio | verdict | NPSHa 60C | NPSHa 80C | NPSHa 70C | NPSHA 75 C
rho | 997 | 0 | 8.0326 | 0 | 3.1 | 4.9326 | 2.5912 | 25 | 3.2 | 997 | 7.7459 | 4.0359 | 2.0878 | Safe | 6.4437 | 3.6553 | 5.3091 | 4.5579
z_suction | -2 | 8 | 8.029 | 0.0036833 | 3.1 | 4.929 | 2.59 | 60 | 19.9 | 983 | 6.157 | 2.447 | 1.6596 | Safe | 6.4401 | 3.6516 | 5.3054 | 4.5543
|  | 16 | 8.0179 | 0.014733 | 3.1 | 4.9179 | 2.5864 | 70 | 31.2 | 978 | 5.0223 | 1.3123 | 1.3537 | Safe | 6.429 | 3.6406 | 5.2944 | 4.5432
k_s | 5.7551e-05 | 24 | 7.9995 | 0.033149 | 3.1 | 4.8995 | 2.5805 | 75 | 38.6 | 975 | 4.2712 | 0.56116 | 1.1513 | Marginal | 6.4106 | 3.6221 | 5.276 | 4.5248
|  | 32 | 7.9737 | 0.058932 | 3.1 | 4.8737 | 2.5722 | 80 | 47.4 | 972 | 3.3685 | -0.34148 | 0.90796 | Cavitates | 6.3848 | 3.5964 | 5.2502 | 4.499
Q_operating | 70.59 | 40 | 7.9406 | 0.092081 | 3.1 | 4.8406 | 2.5615 | 90 | 70.1 | 965 | 1.0116 | -2.6984 | 0.27268 | Cavitates | 6.3517 | 3.5632 | 5.217 | 4.4659
npshr_op | 3.71 | 48 | 7.9 | 0.1326 | 3.1 | 4.8 | 2.5484 | [7 empty] | 6.3112 | 3.5227 | 5.1765 | 4.4253
|  | 56 | 7.8522 | 0.18048 | 3.1 | 4.7522 | 2.533 | [7 empty] | 6.2633 | 3.4748 | 5.1286 | 4.3775
|  | 64 | 7.7969 | 0.23573 | 3.3 | 4.4969 | 2.3627 | [7 empty] | 6.208 | 3.4196 | 5.0734 | 4.3222
|  | 72 | 7.7343 | 0.29834 | 3.8 | 3.9343 | 2.0353 | [7 empty] | 6.1454 | 3.3569 | 5.0108 | 4.2596
|  | 80 | 7.6643 | 0.36833 | 4.2 | 3.4643 | 1.8248 | [7 empty] | 6.0754 | 3.287 | 4.9408 | 4.1896
|  | 88 | 7.587 | 0.44567 | 5.3 | 2.287 | 1.4315 | [7 empty] | 5.9981 | 3.2096 | 4.8634 | 4.1123
|  | 96 | 7.5023 | 0.53039 | 6.3 | 1.2023 | 1.1908 | [7 empty] | 5.9134 | 3.1249 | 4.7787 | 4.0275

## Sheet6
Failure mode | Effect | Cause | How to catch or prevent it | S | O | D | RPN
Cavitation | Impeller pitting, noise, vibration, loss of head | NPSHa below NPSHr: hot water, suction lift, suction friction, high flow | Keep water below about 71 °C (30% margin). Keep the suction pipe short. Listen for a gravel-like noise, watch vibration | 8 | 5 | 5 | 200
Impeller wear or erosion | Head and flow slowly fall | Cavitation, sand or solids in the water | Compare against the pump curve periodically. Fit a strainer | 6 | 5 | 6 | 180
Blocked suction strainer or pipe | Suction friction rises and NPSHa falls, which can cause cavitation | Debris, scale | Suction pressure gauge, clean the strainer on a schedule | 7 | 6 | 4 | 168
Loss of prime or dry running | Overheating, seal and bearing damage | Water level drops, air leak on the suction side (the 2 m lift makes this more likely) | Low-level cutoff, check the foot valve, keep the suction pipe airtight | 9 | 4 | 4 | 144
Bearing failure | Vibration, pump seizes | Misalignment, poor lubrication | Vibration and temperature checks, lubrication schedule | 7 | 4 | 5 | 140
Fouled discharge pipe | Flow falls (your “dirty pipe” case: 79.4 down to 63.6 m³/h) | Scale, corrosion | Compare flow and head with the clean-pipe curve | 5 | 6 | 3 | 90
Mechanical seal leakage | Water loss, bearing damage | Wear, dry running | Visual leak checks | 5 | 6 | 3 | 90